THE SPECIFICATIONS (DRAFT - SUBJECT TO CHANGE)

The following information has been extracted from the Tender Document:

INTRODUCTION

1.	Tenders are invited on a Lot basis and Tenderers should note that contracts may be awarded to one or more suppliers:

LOT 1 – Services for The Felixstowe Dock and Railway Company;

LOT 2 – Services for Harwich International Port Limited; and

LOT 3 – Services for Thamesport (London) Limited.

2.	Each Port is operated by a separate subsidiary of Hutchison Ports (UK) Limited and each subsidiary company shall be responsible for meeting the obligations in the agreement set out in the Form of Contract (“Agreement”) for their respective port.

3.	Site visits to the Ports are mandatory before submitting Tender responses.  Equipment condition reports will be available to view at the site visits.

4.	The commencement date of the Agreement(s) will be 1 March 2022

LOT 1

SPECIFICATION FOR THE SERVICES FOR THE FELIXSTOWE DOCK AND RAILWAY COMPANY

- INTRODUCTION

1.1	The services detailed within this Specification (“Maintenance Services”) are to be carried out at the Port of Felixstowe, Suffolk (“Port”).

1.2	The sewer pit plant (the “Plant”) that requires maintenance under the Agreement is as follows:

- Forty-three (43) mechanical sewer pumping stations;

- Three (3) surface water pumping stations;

- One (1) floating marsh pump; and

- One (1) Klargester treatment plant.

1.3	The Tenderer, hereafter referred to as the “Contractor” is deemed to have examined the Specification, Form of Contract and all relevant information and have included for everything necessary or reasonably implied to complete the whole of the Maintenance Services.

1.4	The Contractor will be held to have familiarised itself with and have knowledge of all site conditions, both on and off shore, Port conditions, wave and tide records, weather, all site data available, means of access and the locality of existing plant.

1.5	The Contractor shall be solely responsible for completing log books for each item of plant, which shall be subject to audit by the Purchaser. These log books must also be kept electronically and saved on a CD/DVD. The electronic records will be presented by (e-mail) to the Purchaser’s Building Services Help Desk on a monthly basis. This information shall remain the property of the Purchaser at all times and the information shall be produced to the Purchaser on CD/DVD on demand or on the natural expiry or termination of the Agreement for any reason.

1.6	The Contractor shall attend regular progress meetings at the Port, where reports shall be provided that contain the following information:

- routines completed prior to invoices being received;

- monthly condition reports; and

- a programme for non-essential replacements/repairs.

1.7	The Contractor shall report to the Building Services Help Desk upon arrival and departure on each visit to the Port.

1.8	The Contractor’s performance will be measured with reference to Key Performance Indicators.  See Schedule 3 of the Agreement.

1.9	The Contractor’s personnel will be required to attend a MANDATORY Port Health and Safety induction prior to obtaining an IDACS pass card. No access to secure areas shall be granted without a pass card.

- SCOPE OF WORK

2.1	The purpose of the maintenance of the Plant is to provide the following:

2.1.1	to detect and monitor the development of defects so that essential maintenance can be planned and undertaken before a failure occurs;

    - to service and maintain the Plant to prevent defects and to obtain condition reports to ensure compliance with the Agreement and to submit maintenance proposals designed to prevent failures;

    - to collect information relating to the condition of the Plant over the period of the Agreement in order to facilitate the development of a policy to ensure safe, cost effective maintenance but above all to ensure the safety of all personnel.

2.2	The maintenance provisions required under the Agreement are:

2.2.1	jet cleaning of the chambers and pipes;

2.2.2	servicing of the pumps, floats and all electrical items;

2.2.3	greasing of covers to ease removal each time a cover is lifted;

2.2.4	repairs to pumps, floats and electrics as agreed with the Purchaser;

2.2.5	emergency call outs;

2.2.6	on occasion the Purchaser may require the removal off site of waste by tanker; and

2.2.7	2 x 25 litre multi-strain fluid and 2 x 5kg degreaser block changed every 50 days and 1 x 25 litre multi-strain fluid changed every 4 weeks and 1 x 5kg degreaser block changed every 8 weeks.

2.3	The frequency of the Maintenance Services shall be as per the sewer pit maintenance schedule as detailed at Table 1B- ‘Frequency of Service Periods’ of this Specification. The frequency of the Maintenance Services may be adjusted by the Purchaser in the course of the Agreement to reflect changing requirements and problem areas. In the event that there is a decrease or increase in the level of Maintenance Services required the Contract Price (as defined in the Agreement) will be varied and agreed between the parties.

2.4	Upon completion of the Maintenance Services on each visit the Contractor shall provide the Purchaser with a service sheet for each item of the Plant serviced providing details of the inspection carried out, amount of chemicals used, electrical readings and any repairs carried out or required.  Any repairs to be carried out will be subject to authorisation by the Building Services Help Desk prior to commencement.

2.5	As part of the reporting process the Contractor shall produce a list of future works that may be undertaken as part of the Agreement or as distinct work packages to be tendered separately in accordance with the Purchaser’s Purchasing Policy.  In the report the Contractor will categorise the work in accordance with the following priorities:

High		:	within four (4) hours;

Medium	:	priority within five (5) days;

Low		:	priority at an agreed date; and

Monitor	:	no action required at the moment apart

from monitoring on a regular basis or more often as advised by the Purchaser.

The Purchaser reserves the right to withhold payment if these reports are not provided.

2.6	All consumables deemed necessary for the Contractor to perform all maintenance and minor repairs including but not limited to replacement of bulbs in beacons, replacement of seals, replacement of fuses and replacement of floats are included within the Contract Price.  The Purchaser shall not be liable for any further charges for these types of materials.

2.7	Servicing of the pumps, floats and all electrical items, shall include but not be limited to the following checks:

- lift pump and clean;

- check condition of pump power supply cable and associated glands;

- examine stator housing for water;

- examine oil housing for water;

- check impeller for wear;

- examine wear ring;

- check route/strainer and clean as necessary;

- assess bearing condition;

- check lifting chain/cables;

- check operation of reflux valves and wash out as necessary;

- check condition of pipework;

- insulation resistance test circuit cable and record reading;

- check overload setting (record);

- record earth loop resistance;

- clean control panel;

- check fuses for security and fasten as necessary;

- check operation of heater;

- check and replace indicators as necessary;

- check alarm operation;

- check and clean floats.  Adjust and tidy cables as necessary;

- clean kiosk inside and out;

- check installation for damage;

- check installation for security;

- check sump condition (report);

- check system operation;

- jet wash pit; and

- clean and grease covers.

This level of detail is a requirement on all Maintenance Services undertaken by the Contractor.

2.8	Table 1A provides a description of the Plant.

3.0	HEALTH AND SAFETY

3.1	Works on the Plant shall be fully compliant with the Confined Spaces Regulations 1997 and to this end a permit of work is required.  This can be obtained through the Building Services Help Desk at each visit.

3.2	The Contractor’s attention is drawn to Weils Disease (Leptospirosis) which is a reportable disease carried by rats, sewerage etc. and can be passed on to humans hence the Contractor shall take all precautions to prevent any infection.

3.3	The Contractor will be required to provide a Construction Phase Plan in accordance with the Construction (Design and Management) Regulations 2015.

4.0 	EMERGENCY CALL OUT SERVICE

The Contractor shall provide an emergency call out service twenty-four hours a day, seven days a week, three hundred and sixty-five days per annum and provide a suitably qualified team covering labour onsite within four (4) hours of notification, and in this respect provide at all times, including holiday cover, a single named contact and telephone number of a supervisor responsible for coordination of all emergencies.  The emergencies will be for e.g.:

- failed Plant;

- overflowing pits; and

- floods

5.0	LEVELS OF SKILL

It is a requirement of the Agreement that all of the Contractor’s staff have the appropriate level of skill and competency required to undertake the Maintenance Services.  The Contractor shall demonstrate such level of skill and competency prior to carrying out any work at the Port.

TABLE 1A

PORT OF FELIXSTOWE DESCRIPTION OF PLANT

| Pit No. | Asset No. | Location | Type | Notes |
| --- | --- | --- | --- | --- |
| 1 | H2644 | 70 Shed | Dual Biwater Pump Station | Office end of building, controls inside building |
| 2 | H4399 | Trinity Fork Lift Park | Single ABS Piranha S12/2 | Near the entrance barrier when entering Trinity from Oysterbed Road |
| 3 | H2231 | Trinity North Quay Office | Dual Biwater Pump Station VP220-024-6 | Seaward side of quay office. Controls are on end of sub-station on landward side of office |
| 4 | H2544 | Trinity North Ingate | Dual Gorman-Rupp Pump Station JW V220-4P 4Kw | Pit is relatively near the fuel tank. Controls are under seaward end of in gate canopy |
| 5 | H1543 | Centenary House | Gorman-Rupp | North end of building. Controls are on the end of sub-station 29 on the other side of building |
| 6 | H2648 | Old Anglo European site | GR JWV408 Dual Pump Station | In the car park. Controls are on the side of the building |
| 7 | H1539 | Freightliner North | Single Faggiolati Pump No data plate | North end of Terminal |
| 8 | H4414 | Trimley House | Flygt 3085.181 Pump Station | By the entrance to the building |
| 9 | H2230 | Old Osprey yard near 94 shed | ABS Pump Station | In the car park area toward gate complex |
| 10 | H1542 | Walton/Trinity Outgate | Wallwin Pump Station | South and seaward end of out gate complex. Controls are in box under nearby lighting tower |
| 11 | H0739 | Police Gate No.2 | Wallwin Pump Station & Gorman-Rupp | Landward side of Central Workshop against the fence with No 2 Police gate |
| 12 | H1538 | Enso Gate (77 Park) | Flygt MP3068 Dual Pump Station | Bottom corner of 77 Park |
| 13 | H0738 | 91/92 Shed | Wallwin Pump Station | Southern end of Central Road on island between 91 shed working area and the road |
| 14 | H0737 | Dooley Quay | Wal1win | Landward side of quay office. Controls are in adjacent toilet block |
| 15 | H0744 | Dooley Management Office | Flygt MP3068 Pump Station | Small building just seaward of Dooley Management Office |
| 16 | H0735 | 30 Shed | Dual Grundfos Pumps Type SEV.80.80.22.4 | Southern landward end of warehouse |
| 17 | H0733 | Police Gate No.1 | Mono 09083 Pump Station | Seaward end of building |
| 18 | H0731 | Substation Road | 2 No Flygt NP3085 2kw 415 volts Tag No 0880101 & 0880103 | In lay by on right side 100m down the road |
| 19 | H0734 | Rail Yard by loco pit | Dual Wallwin Pump Station Hook up Type No Data Plate | Next to the ramp and pit in the training area in the rail yard |
| 20 | H0729 | 14/83 Shed | Flygt NS3085 3 phase 24kw Tag No 0880104 | In the road between 13/14 shed at the town end |
| 21 | H0730 | Trelawny House/14 Shed | Flygt N3085 x 2 Pump Station | On side of 14 shed, on road between 13/14 sheds |
| 22 | H1540 | Police Station | Biwater Pump Station | North side of building where traffic exits. Controls are on south side of the building |
| 23 | H0742 | Landguard Engineering | ABS Piranha 526/2 3 phase 2.5a Pump Station | On fence with road to customs, best accessed from this road rather than through the workshop |
| 24 | H0741 | Freightliner South | 2 No Flygt NP3085 2kw Pumps tag no 0880100 & 0880102 | North End of the Freightliner terminal, side of road towards 75 Park |
| 25 | H2232 | Tomline House | Dual Biwater Pump Station Gorman-Rupp | In the car park |
| 27 | H0743 | Wickenden House car park | Mono Dual Pump Station AA1-AB1 | Middle of car park, Next to Substation R5909 |
| 28 | H1541 | Wickenden House | Biwater Pump Station | North West corner of building |
| 29 | H2966 | Dooley Canteen | Biwater Dual Pump Station Gorman-Rupp | Canteen car park. Controls are on wall of canteen building |
| 30 |  | Orwell Engineering (compit) | Flygt 3057 single 3 phase Pump Station |  |
| 31 | H4383 | Orwell Engineering (foul) | Flygt 3085 181 Dual Pump Station | Pit located mid front of building controls |
| 32 | H4383 | Orwell Engineering (surface) | Flygt 3067 180 Dual Pump Station | Pit in RTG wash down area, controls |
| 33 | H4420 | Trimley Marsh Dyke Pump | M2.5O M8 Single Pump Station | Trimley Nature Reserve |
| 34 |  | Cold Store Roundabout | Dual Grundfos AP60/B Pump Station |  |
| 35 | E0080 | Old Building Services | SXM3 Pump |  |
| 36 |  | Freedoms Yard | DAB Dual 3068 Pump Station |  |
| 37 | H4955 | Substation Road | Mono AA Dual Pump Station |  |
| 38 |  | 75 Park Training Area | Faggiolati GNASHER 6T 3 phase Single Pump Station |  |
| 39 |  | 86 Park | Homa GRP168BD Single Pump Station APG50.09.3 |  |
| 40 |  | Tank Farm | Johnson FRES80 x 4 Surace mounted Surface Water Pumps |  |
| 41 | H3514 | 94 Shed | 3068 Duty Standby Compit |  |
| 42 | H4608 | PJ Services | 3068 Duty Standby Compit |  |
| 43 |  | FSR near Fire Pump House | 3068 Duty Standby Duel Pump Station |  |
| 44 |  | Central Rail | Klargester S.T.P |  |
| 45 |  | Landguard Viewing Centre | Duel 3102 Pumping Station |  |
| 46 | H4428 | Seafarers Centre (only breakdowns) |  |  |
| 49 |  | New Inspection Facility, adjacent to 70 Shed (under construction completion 29 November 2021) |  |  |

TABLE 1 B - FREQUENCY OF SERVICE PERIODS

| Pit No. | Asset No. | Location | Service Periods |
| --- | --- | --- | --- |
| 1 | H2644 | 70 Shed | 18 weeks |
| 2 | H4399 | Trinity Fork Lift Park | 18 weeks |
| 3 | H2231 | Trinity North Quay Office | 18 weeks |
| 4 | H2544 | Trinity North Ingate | 18 weeks |
| 5 | H1543 | Centenary House | 6 weeks |
| 6 | H2648 | Old Anglo European Site | 18 weeks |
| 7 | H1539 | Freightliner North | 18 weeks |
| 8 | H4414 | Trimley House | 18 weeks |
| 9 | H2230 | Old Osprey Yard near 94 shed | 18 weeks |
| 10 | H1542 | Walton/Trinity Outgate | 18 weeks |
| 11 | H0739 | Police Gate No.2 | 6 weeks |
| 12 | H1538 | Enso Gate (77 Park) | 18 weeks |
| 13 | H0738 | 91/92 Shed | 18 weeks |
| 14 | H0737 | Dooley Quay | 18 weeks |
| 15 | H0744 | Dooley Management Office | 18 weeks |
| 16 | H0735 | 30 Shed | 18 weeks |
| 17 | H0733 | Police Gate No.1 | 18 weeks |
| 18 | H0731 | Substation Road | 6 weeks |
| 19 | H0734 | Rail Yard by loco pit | 18 weeks |
| 20 | H0729 | 14/83 Shed | 18 weeks |
| 21 | H0730 | Trelawny House/14 Shed | 6 weeks |
| 22 | H1540 | Police Station | 18 weeks |
| 23 | H0742 | Landguard Engineering | 18 weeks |
| 24 | H0741 | Freightliner South | 18 weeks |
| 25 | H2232 | Tomline House | 6 weeks |
| 27 | H0743 | Wickenden House car park | 18 weeks |
| 28 | H1541 | Wickenden House | 18 weeks |
| 29 | H2966 | Dooley Canteen | 6 weeks |
| 30 |  | Orwell Engineering (compit) | 18 weeks |
| 31 | H4383 | Orwell Engineering (foul) | 18 weeks |
| 32 | H4383 | Orwell Engineering (surface) | 18 weeks |
| 33 | H4420 | Trimley Marsh Dyke Pump | 18 weeks |
| 34 |  | Cold Store Roundabout | 18 weeks |
| 35 | E0080 | Old Building Services | 18 weeks |
| 36 |  | Freedom’s yard | 18 weeks |
| 37 | H4955 | Substation Road | 18 weeks |
| 38 |  | 75 Park Training Area | 18 weeks |
| 39 |  | 86 Park | 18 weeks |
| 40 |  | Tank Farm (surface) | 6 weeks |
| 41 | H3514 | 94 Shed | 18 weeks |
| 42 | H4608 | PJ Services | 18 weeks |
| 43 |  | FSR near Fire Pump House | 18 weeks |
| 44 |  | Central Rail Building | 18 weeks |
| 45 |  | Landguard Viewing Centre | 18 weeks |
| 46 | H4428 | Seafarers Centre (only breakdowns) | Breakdowns only |
| 49 |  | New Inspection Facility, adjacent to 70 Shed (under construction completion 29 November 2021) | 18 weeks |

LOT 2

SPECIFICATION FOR THE SERVICES FOR HARWICH INTERNATIONAL PORT LIMITED

- INTRODUCTION

1.1	The services detailed within this Specification (“Maintenance Services”) are to be carried out at Harwich International Port, Essex (“Port”).

1.2	The sewer pumping installations and equipment that requires maintenance under the Agreement is as follows:

- Ten (10) mechanical foul water pumping stations;

- Three (3) mechanical surface water pumping stations;

- Two (2) mechanical trade effluent pumping stations; and

- One (1) foul water treatment plant.

1.3	The Tenderer, hereafter referred to as the “Contractor” is deemed to have examined the Specification, Form of Contract and all relevant information and have included for everything necessary or reasonably implied to complete the whole of the Maintenance Services.

1.4	The Contractor will be held to have familiarised itself with and have knowledge of all site conditions, both on and off shore, Port conditions, wave and tide records, weather, all site data available, means of access and the locality of existing plant.

1.5	The Contractor shall be solely responsible for completing log books for each item of the plant, which shall be subject to audit by the Purchaser. These log books must also be kept electronically and saved on a CD/DVD. The electronic records will be presented by (e-mail) to the Purchaser’s Engineering Department on a monthly basis. This information shall remain the property of the Purchaser at all times and the information shall be produced to the Purchaser on CD/DVD on demand or on the natural expiry or termination of the Agreement for any reason.

1.6	The Contractor shall attend regular progress meetings at the Port, where reports shall be provided that contain the following information:

- routines completed prior to invoices being received;

- condition reports;

- a programme for non-essential replacements/repairs.

1.7	The Contractor shall report to the Engineering Department upon arrival and departure of each visit to the Port.

1.8	The Contractor’s performance will be measured with reference to Key Performance Indicators.  See Schedule 3 of the Agreement.

1.9	The Contractor’s personnel will be required to attend a MANDATORY Port Health and Safety induction prior to obtaining a security access pass card. No access to secure areas shall be granted without a pass card.

- SCOPE OF WORK

2.1	The purpose of the Maintenance Services is to provide:

2.1.1	planned preventative maintenance to sewer pumping installations and equipment in order to prevent equipment failure;

2.1.2	repairs to sewer pumping installations and equipment following planned preventative maintenance in order to prevent equipment failure; and

2.1.3	emergency repairs to sewer pumping installations and equipment following equipment failure both during and outside of normal working hours.

2.2	The frequency of the Maintenance Services shall be three (3) visits per annum at dates to be specified by the Purchaser. The frequency of the Maintenance Services may be adjusted by the Purchaser in the course of the Agreement to reflect changing requirements and problem areas. In the event that there is a decrease or increase in the level of Maintenance Services required, the Contract Price as defined in the Agreement will be varied and agreed between the parties.

2.3	Upon completion of each Maintenance Services visit, the Contractor shall provide the Purchaser with a service sheet for each item of the plant serviced providing details of the work carried out, amount of chemicals used, electrical readings and any repairs carried out or required.  Any repairs to be carried out will be subject to authorisation by the Engineering Department prior to commencement.

2.4	As part of the reporting process the Contractor shall produce a list of future works that may be undertaken as part of the Agreement or as distinct work packages to be tendered separately in accordance with the Purchaser’s Purchasing Policy.  In the report the Contractor shall categorise the work in accordance with the following priorities:

High		:	within four (4) hours;

Medium	:	priority within five (5) days;

Low		:	priority at an agreed date; and

Monitor	:	no action required at the moment apart

from monitoring on a regular basis or more often as advised by the Purchaser.

The Purchaser reserves the right to withhold payment if these reports are not provided.

2.5	All consumables deemed necessary for the Contractor to perform all maintenance and minor repairs including but not limited to replacement of bulbs in beacons, replacement of seals, replacement of fuses and replacement of floats are included within the Contract Price.  The Purchaser shall not be liable for any further charges for these types of materials.

2.6	Servicing of the pumps, floats and all electrical items, shall include but not be limited to the following:

- Lift pump(s) and clean;

- Check motor / pump cables for wear and water ingress;

- Check motor windings for continuity and insulation integrity;

- Examine stator housing for water ingress;

- Examine oil housing for water ingress and replace oil if contaminated;

- Check impeller for wear, debris and damage (unblock as required);

- Check wear ring(s);

- Check route/strainer and clean as necessary;

- Assess motor / pump bearing condition;

- Check condition and serviceability of pump lifting system;

- Check operation and isolation of reflux valves (wash out as necessary);

- Check condition of pipework;

- Insulation resistance test circuit cable and record reading;

- Check overload setting (record);

- Check and record earth loop resistance;

- Check condition and serviceability of control panel.  Clean control panel;

- Check and adjust all pump controls as necessary.  Check fuses for security and fasten as necessary.  Check and replace any indicators as necessary;

- Check and test alarm operation;

- Check and clean level control floats.  Adjust and tidy cables as necessary;

- Check condition of control panel kiosk.  Clean kiosk inside and out;

- Check installation for damage;

- Check installation for security;

- Check sump condition (report);

- Check system operation;

- Manually lower waste level and de-sludge sump annually;

- Jet wash pit;

- Review appearance of Biomass (treatment plant);

- Check the general condition (treatment plant);

- Check that inlet and outlet pipes are clear and remove debris if necessary (treatment plant);

- Check that dosing bucket(s) are transferring liquid consistently (treatment plant);

- Check correct operation of pump, floats and alarms (treatment plant);

- Check loss of rotation warning device for correct operation (treatment plant); and

- leave the site clean and tidy.

This level of detail is a minimum requirement on all Maintenance Services undertaken by the Contractor.

2.7	Table 2A provides a description of the sewer pumping installations and equipment together with frequency of Maintenance Services.

3.0	HEALTH AND SAFETY

3.1	Works on the sewer pits shall by fully compliant with the Confined Spaces Regulations 1997 and to this end a permit of work is required.  This can be obtained through the Engineering Department at each visit.

3.2	The Contractor’s attention is drawn to Weils Disease (Leptospirosis) which is a reportable disease carried by rats, sewerage etc. and can be passed on to humans hence the Contractor shall take all precautions to prevent any infection.

3.3	The Contractor will be required to provide a Construction Phase Plan in accordance with the Construction (Design and Management) Regulations 2015.

4.0 	EMERGENCY CALL OUT SERVICE

The Contractor shall provide an emergency call out service twenty-four hours a day, seven days a week, three hundred and sixty-five days per annum and provide a suitably qualified team covering labour onsite within four (4) hours of notification, and in this respect provide at all times, including holiday cover, a single named contact and telephone number of a supervisor responsible for coordination of all emergencies.

5.0	LEVELS OF SKILL

It is a requirement of the Agreement that all of the Contractor’s staff have the appropriate level of skill and competency required to undertake the Maintenance Services.  The Contractor shall demonstrate such level of skill and competency prior to carrying out any work at the Port.

Table 2A - Harwich Pumping Stations

| Asset No. | Type | Equipment | Location | Service Frequency |
| --- | --- | --- | --- | --- |
| U0101 | Surface Water Pumping Station | Twin Flygt 3127 | 5.5 Acres | 4 monthly |
| U0102 | Foul Water Pumping Station | Single Grundfos APG 240 / 150 | Engineering Workshop | 4 monthly |
| U0103 | Trade Effluent Pumping Station | Single AMA Porter 602 | Engineering Steam Cleaning Facility | 4 monthly |
| U0104 | Surface Water Pumping Station | Single Flygt 3085 | Cruise Car Park 3 | 4 monthly |
| U0105 | Foul Water Pumping Station | KSB KRTF 80-200 / KSB Amarex F80-210 | Car Terminal | 4 monthly |
| U0106 | Foul Water Pumping Station | KSB DUL FRTF65 / AMA Porta 601 | Station Road | 4 monthly |
| U0107 | Foul Water Pumping Station | Twin Klargester 505 | Forward Holding Area | 4 monthly |
| U0108 | Foul Water Pumping Station | Single Ri-Mon | Freight Reception Area | 4 monthly |
| U0109 | Foul Water Pumping Station | Single Flygt MP3085 | Freight Shed 1 | 4 monthly |
| U0110 | Foul Water Pumping Station | Single Flygt 3085 | Trailer Park | 4 monthly |
| U0111 | Foul Water Pumping Station | Single DAB F&KU | Container Terminal | 4 monthly |
| U0112 | Surface Water Pumping Station | Twin Grundfos AP65 | Engineering Workshop | 4 monthly |
| U0113 | Trade Effluent Pumping Station | Twin AMA Porta Sol | Vehicle Cleaning & Refuelling Facility | 4 monthly |
| U0114 | Foul Water Treatment Plant | Kingspan BioDisc BA | Warehouse 2 | 4 monthly |
| U0115 | Foul Water Pumping Station | Single FEKA 750 | Brickyard 5.5 Acres | 4 monthly |
| U0116 | Foul Water Pumping Station | Single Flygt 3057.151 | HGV Parking Area | 4 monthly |

LOT 3

SPECIFICATION FOR THE SERVICES FOR THAMESPORT (LONDON) LIMITED

1.0	INTRODUCTION

1.1	The services detailed within this Specification (“Maintenance Services”) are to be conducted at London Thamesport (the “Port”).

1.2	The Tenderer is hereafter referred to as the “Contractor”. The Contractor’s personnel will be required to attend a MANDATORY Port Health and Safety induction prior to obtaining an IDACS pass card. No access to secure areas shall be granted without a pass card.

1.3	Due to the size and nature of the Port site and the requirement in accordance with paragraph 1.2 above, it is preferable that the Contractor provides dedicated Engineers to carry out the Maintenance Services.  See Appendix 3 Documents to be provided by the Contractor.

1.4	The Contractor will be required to provide a dedicated account manager to the Purchaser.  See Appendix 3 Documents to be provided by the Contractor.

1.5	The Contractor’s performance will be measured with reference to Key Performance Indicators.  See Schedule 3 of the Agreement.

2.0	SEWER PUMP MAINTENANCE SERVICES

2.1	The sewer pit and pump equipment that requires maintenance under the Agreement is located at various locations as detailed in Appendix 1A and consists of 10 stations, described as:

- Station 1	Entec Biotec Sewage Treatment Plants;

- Station 2	Klargester Biodisc Sewage Treatment Plants;

- Station 3	Ebara Foul Duplex Pumping Station;

- Station 4	Ebara Foul Duplex Pumping Station;

- Station 5	Foul Duplex Pumping Station;

- Station 6	Foul Duplex Pumping Station;

- Station 7	Effluent Duplex Pumping Station;

- Station 8	Conder Package Sewage Treatment Plant;

- Station 9	Conder Package Sewage Treatment Plant; and

- Station 10	Foul Pumping Station.

Note: Station 11 detailed in Appendix A - Plans does not form part of the Agreement.

Additionally the Contractor will be required to empty the 4000g steam bay wash pit at the Port that builds up with oily waste off tugs, forklifts and other vehicles.   As the requirement for emptying varies according to weather conditions, the Contractor must supply a price per empty, and only empty the wash pit when requested by the Purchaser.

2.2	The Contractor will have been deemed to have examined the relevant drawings, Specification and the terms and conditions of the Form of Contract and all other relevant information and have included for everything necessary or reasonably implied to complete the whole of the Maintenance Services.

2.3	The Contractor will be held to have familiarized himself with all site conditions, both on and off shore, Port conditions, wave and tide records, weather, all site data available, means of access and the locality of the existing plant.

2.4	The Contractor shall be solely responsible for completing log books for each item of the plant, which shall be subject to audit by the Purchaser’s personnel. These log books must also be kept electronically.  The electronic records should be presented (by e-mail) to the Port’s Engineering Department on request. The information remains the property of the Purchaser at all times and will be passed to the Purchaser on expiry or termination of the Agreement.

2.5	The Contractor shall attend regular progress meetings at the Port, where reports shall be provided that contain the following information:

(a)	reports on routines completed prior to any invoice being received;

(b)	condition reports; and

(c)	a programme for non-essential replacements/repairs.

2.6	The Contractor shall report to the Engineering Department upon arrival and departure on each visit to the Port.

3.0      SCOPE

3.1	The purpose of the maintenance is:

3.1.1	to detect and monitor the development of defects so that essential maintenance can be planned and undertaken before a failure occurs;

3.1.2	to service and maintain the sewer pit and pump equipment to prevent defects and to obtain condition reports to ensure compliance with the Agreement and to submit maintenance proposals designed to prevent failures; and

3.1.3	to collect information relating to condition over the period of the Agreement in order to facilitate the development of a policy to ensure safe, cost effective maintenance but above all to ensure the safety of all personnel.

3.2	The Maintenance Services required under the Agreement are:

3.2.1	jet cleaning of the chambers;

3.2.2	servicing of the pumps, floats and all electrical items;

3.2.3	greasing of covers to ease removal each time a cover is lifted;

3.2.4	repairs to pumps, floats and electrics as agreed with the Purchaser;

3.2.5	emergency call outs; and

3.2.6	the Purchaser may require the removal off site of waste by tanker.

3.3	The Contractor shall make two (2) visits per annum to the Port to provide the Maintenance Services at a time to be agreed by the Purchaser. The frequency of the Maintenance Services may be adjusted in the course of the Agreement to reflect changing requirements and problem areas.

3.4	Upon completion of the Maintenance Services on each visit the Contractor shall provide the Purchaser with a hard copy written service sheet for each item of the plant serviced providing details of the inspection carried out, amount of chemicals used, electrical readings and any repairs carried out or required.  Any repairs to be carried out will be subject to authorisation by the Port’s Engineering Department prior to commencement.

3.5	As part of the reporting process, following each visit the Contractor shall produce a list of future services that may be undertaken as part of the Agreement or as distinct work packages tendered for separately.  In the report the Contractor will categorise the work in accordance with the following priorities:

High		:	within four (4) hours;

Medium	:	priority within five (5) days;

Low		:	priority at an agreed date; and

Monitor	:	no action required at the moment apart

from monitoring on a regular basis or more often as advised by the Purchaser.

The Purchaser reserves the right to withhold payment if these reports are not

provided.

3.6	The Purchaser reserves the right to tender services in connection with the Agreement that breach its internal annual threshold values for tendered services.

3.7	All minor consumables such as greases, cleaning agents, seals etc. deemed necessary for the Contractor to perform all Maintenance Services are included within the Charges in Appendix 2.  The Purchaser shall not be liable for any further charges for these types of consumable materials.

3.8	Routine servicing of the pumps, floats and all electrical items, including but not limited to, the following checks:

3.8.1	Submersible pumps:

(a)	report to the Engineering Department on arrival at the Port.  Discuss with Purchaser any problems with systems operation;

(b)	carry out risk assessments before starting work;

(c)	ensure any station details that are not present on the report sheet are documented on the sheet, to enable Purchaser records to be updated;

(d)	on arrival observe status of all panel indicators, recording on service sheet any failures found;

(e) 	megger pump windings.  If pump readings are below one (1) meg ohm contact the Purchaser for previous history and agreed action;

(f)	check motor current and enter details on service sheet.  Compare readings with full load current (FLC) on motor and overload settings.  Record hours run readings where applicable;

(g)	if telemetry exists, stimulate alarm and check with service office that it has been received;

(h)	Test pumps work on hand control, investigate any malfunction;

(i)	Check and ensure all terminals within control panel are tight and that the heater is working;

(j)	ensure floats are clean, free and untangled.  Inspect float and pump suspension cables for stress failure in flexing zone.  Check automatic operation by tilting floats manually, including function of high level alarm;

(k)	clean off any fat build up around guiderails and other components affecting level control;

(l)	check junction box is adequately sealed and that cable glands are secure.  If low insulation readings found, carry out further checks to investigate cause;

(m)	operate and lubricate gate valve and check correct operation of non-return valve;

(n)	check earth bonding status including sump/kiosk and integrity of incoming supply;

(o)	ensure control enclosure is tidy and clean.  Oil locks and hinges.  Remove all cleaning materials and rubbish.  Check that cable duct is adequately sealed, reseal if necessary;

(p)	recheck that power is switched on and system set to automatic;

(q)	raise pumps and inspect for excessive noise/vibration.  Check oil and replace if contaminated.  Check for impeller wear or damage and confirm correct rotation; and

(r)	leave the site secure and tidy.

3.8.2	Sewage Treatment Plants

- report to Engineering Dept. on arrival at Port.  Discuss with Purchaser any

problems with systems operation;

(b)	carry out risk assessments before starting work;

(c)	ensure any station details that are not present on report sheet are documented on sheet, to enable Purchaser records to be updated;

(d)	carry out general inspection of the exterior of the tank and access covers.  Ensure damage and/or shortages are recorded on the service sheet:

(e)	observe status and operation of all panel indicators (if present) recording on service sheet any failures found;

(f)	megger pump/blower windings.  If pump readings are below one (1) meg ohm contact relevant service coordinator for previous history and agreed action;

(g)	check motor current and enter details on service sheet.  Compare readings with full load current (FLC) on motor and overload settings.  Record hours run readings where applicable;

- check timer settings and record if applicable;

- check and ensure all terminals within control panel are tight and that heater (if fitted) is working;

(j)	if telemetry exists, stimulate alarm and check with service office that it has been received;

(k)	test pumps work on hand and/or automatic control, investigate any malfunction;

(l)	lift pump and check and report on condition of diffusers, impellers and cable;

(m)	ensure floats are clean, free and untangled.  Inspect float and pump suspension cables for stress failure in flexing zone.  Check automatic operation by tilting floats manually, including function of high level alarm;

(n)	clean off any fat build up around pumps and internal tank fittings;

(o)	check junction box (if fitted) is adequately sealed and that cable glands are secure;

(p)	check earth bonding status including sump/kiosk and integrity of incoming supply;

(q)	ensure control enclosure is tidy and clean.  Oil locks and hinges.  Remove all cleaning materials and rubbish.  Check that cable duct is adequately sealed, reseal if necessary;

(r)	check visual appearance of water quality and biological growth throughout plant;

(s)	confirm correct ventilation exists.  Check ventilation pipes for obstruction or blockage;

(t)	check operation of plant aeration;

(u)	recheck that power is switched on and system set to automatic; and

(v)	leave the site secure and tidy.

3.9	Surface Water Interceptors

The surface water interceptors that require maintenance under the Agreement are located at various locations as detailed in Appendix 1A and consist of 10 stations.

Annually, at a time to be agreed with the Purchaser all stations are to be inspected and cleaned, any oil residue sucked out and removed by tanker.

All oil detection alarms are to be serviced and tested in line with manufacturer’s recommendations.

Reports confirming completion of the maintenance and condition of the interceptors to be provided to the Purchaser within five working days of visit.

4.0       CALL OUT SERVICES

4.1	The Contactor shall attend site with suitably qualified, equipped and inducted operatives within four (4) working hours of request by the Purchaser, to respond to emergency requests 24 hours a day, 7 days a week, 365 days a year.

4.2	In such circumstances it is envisaged that the pumping station will need to be pumped out before investigation and repair work can commence to the pump. The Contractor will ensure that any necessary tanker/jetter is also on site and operable within four (4) hours of request.

4.3	In normal circumstances the Purchaser would expect any emergency rectification work to be completed as part of this initial visit. Where this is not possible, a separate report sheet shall be provided to the Purchaser identifying the estimated cost of the remedial works and the timescale required.  The Purchaser shall authorise this estimate prior to any works commencing.

5.0	HEALTH AND SAFETY

5.1	Works on the sewer pits shall by fully compliant with the Confined Spaces Regulations 1997 and to this end a permit of work is required.  This can be obtained through the Port’s Engineering Department at each visit.

5.2	The Contractor’s attention is drawn to Weils Disease (Leptospirosis) which is a reportable disease carried by rats, sewerage etc. and can be passed on to humans hence the Contractor shall take all precautions to prevent any infection.

5.3	The Contractor will be required to carry out a Construction Phase Plan in accordance with the Construction (Design and Management) Regulations 2015.

6.0	LEVELS OF SKILL

It is a requirement of the Agreement that all of the Contractor’s staff have the appropriate level of skill and competency required to undertake the Maintenance Services.  The Contractor shall demonstrate such level of skill and competency prior to carrying out any work at the Port.

CESSPIT CLEANSING SERVICES

- INTRODUCTION

1.1	The Purchaser requires the cleaning and emptying of one cesspit at regular intervals to be advised by the Purchaser from time to time (the “Cesspit Services”).

1.2	The charges for the Cesspit Services (the “Charges”) shall be inclusive of all equipment, consumables (as required), labour, transport and disposal during normal working hours, being 0830 to 1700 hours Monday to Friday.  Any additional unscheduled services shall be known as “Additional Cesspit Services” requested by the Purchaser and shall be charged at the rate per hour as set out in Appendix 2.

1.3	The Contractor shall provide the Purchaser with Waste Transfer Note(s) and service report(s) on each visit.  Each report shall provide the location, order number and number of gallons removed, any cleaning chemicals that have been used during the cleaning process and equipment reports detailing the current state of the equipment, and faulty or damaged equipment.  This documentation is to be received by the Port’s Engineering Department at the end of each visit.

1.4	The Contractor will hold all applicable licenses required to undertake the Cesspit Services and any revocation of licensing must be notified to the Purchaser immediately.

- SCOPE OF SERVICES

The Contractor shall clean and empty the cesspit as detailed below.

- Cesspit requirements:

| Location | Capacity | Estimated Frequency |
| --- | --- | --- |
| Warehouse Offices | 4000 gallons | Once every two to four weeks |

(i)	The frequency for the Cesspit Services shall be advised by the Purchaser at the commencement of the Agreement and will be subject to amendment from time to time by the Purchaser.  The Purchaser will provide the Contractor with a minimum of one week’s notice of its intention to revise the frequency.

(ii) 	The Contractor shall also be responsible for the removal from site and disposal of all waste matter arising from undertaking the Cesspit Services in accordance with the Waste (England & Wales) (Amendment) Regulations 2012.  The disposal charges are included in the Charges set out in Table 1 cesspit cleansing services of Appendix 2.

(iii)	Additional Cesspit Services may be required and the charges applicable are set out in Table 2 cesspit cleansing services of Appendix 2.

(iv)	The Contractor shall provide a response time to site in the event of a call out for Additional Cesspit Services in the table below:

| Within normal working hours of 0830-1700 hours Monday to Friday | hours |
| --- | --- |
| Outside of normal working hours | hours |

- Kitchen Grease Trap: - NOTE: The canteen kitchen is not currently operational and therefore the services detailed here in 2.0(b) are not currently required but Tenderers are requested to provide a charge in Appendix 2 in this respect that will be applicable should the facility be reopened. The Purchaser will provide the Contractor with two weeks’ notice of its intention to reopen the facility.

| Location | Capacity | Estimated Frequency |
| --- | --- | --- |
| Canteen Kitchen Storeroom | 1000 gallons | Once every four weeks |

- The Contractor shall also be responsible for the removal from site and disposal of all waste matter in accordance with the Waste (England & Wales) (Amendment) Regulations 2012.  The disposal charges for this are included in the Kitchen Grease Trap charge per visit as set out in Appendix 2.

- The Contractor shall provide a clean hose dedicated solely for all services undertaken within the kitchen areas, to be kept permanently on site at London Thamesport, stowed out of doors, adjacent to the kitchen.  The Contractor shall comply with all rules, regulations, laws, codes of practice, recommendations relating to food hygiene.

- Additional services in between scheduled visits may be necessary and the charges applicable are as set out in Appendix 2. The response time to site will be as per the table at 2.0(a)(iv) above.

APPENDIX 1A

PORT PLANS

Plan

A location plan is provided at Appendix 1A.  NOTE: Stations numbered 12-22 are for identification purposes only. Similarly, cesspits/tanks are shown which are outside the scope of the Cesspit Services for information/identification purposes only.

PORT OF FELIXSTOWE

HARWICH INTERNATIONAL PORT

LONDON THAMESPORT

LONDON THAMESPORT - SEWERS