| PD0043 | PD Project Feasibility Report |
| --- | --- |

Programme

Project

Document reference

Lift Availability Report (Step Free Access)

|  |  | Signature |  | Date |
| --- | --- | --- | --- | --- |
| Prepared by | N.Foord Engineer (Lifts) | Norman Foord |  | 21-9-2020 |
| Reviewed by | G. Folkes Senior Engineering Leader |  |  | 22/09/2020 |
| Approved by | I confirm that this deliverable meets the requirements of the relevant Pathway Product Description and that all consultation comments have been addressed to the satisfaction of consultees. |
|  | <Name> Sponsor |  |  |  |

| Distributed to | <Name> | <Role> |
| --- | --- | --- |

Document History

| Revision | Date | Summary of changes |
| --- | --- | --- |
| 01 | 15/7/2020 | For Issue |
| 02 | 21/9/2020 | Revised according to project feedback & scope expanded |
| 03 | 9.102020 | Appendix A revised |

# Contents

1    Background	3

2	Main Project Business Benefits	4

3	Feasibility Study Scope	4

APPENDIX A –Lifts in Scope	7

APPENDIX B - Lift Status Panel – images & typical circuit diagram	27

APPENDIX C – Typical LAN connections	29

# Background

## Background Description

Transport for London is committed to making our network even more accessible for all. Many customers rely on real-time reporting of the status and availability of lifts to complete step-free journeys. Any absence, delay or inaccuracy in this information can lead to significant inconvenience or even result in the trip needing to be cancelled.

TfL wish to provide remote real time information on the availability of lifts which assist in Step Free Access to London Underground and Docklands Light Railway (DLR) stations in our own and third party products.  The intention is to provide advance notification to disabled customers so that they can avoid a particular station should a lift used for entering or exiting the station or for interchanges be unavailable at the time.

The scope of this report includes all lifts that provide step free access on the LU & DLR networks plus others such as the Primary Means of Vertical Transportation in stations where the only alternative is to use the stairs. While these lifts may not offer a fully step free journey, they are useful to Persons of Restricted Mobility (PRMs) and this includes people with luggage or pushchairs etc.

The report does not include the few stairlifts that exist on the network.

The Transport Innovation Directorate have produced a market sounding questionnaire (MSQ) for the step-free access lift status problem statement. This report informs the MSQ of the different lift signals across LU to provide high-level key service requirements for responses to the MSQ.

## Business Objectives

To provide remote real time information on the availability of lifts providing access to London Underground and Docklands Light Railway stations for TfL’s channels and third party products.

## Responsibilities

This report has been produced as a desktop exercise by TfL Engineering to advise of the outputs available to confirm lift availability.

## Reporting and Control Requirements

This report is a standalone document used to inform the Real-time Lift Status Information MSQ. Any proposals or solutions for real time information should not affect the safety or normal operations of the lift assets and will require acceptance from TfL Engineering.  Any interfaces with Station Management Systems or upgrading of software will be factory tested before integration to avoid any impact on station operations.

## Risks & Issues

Within the scope of this report the risks are:

Cost and complexity in combining different lift outputs into one system and integration with the existing station management systems due to the high-risk activity of upgrading the station communication software.

# Main Project Business Benefits

To facilitate the completion of any trials that may be carried out as a result of the MSQ by identifying the lifts that we have on the LU & DLR networks and advising what facilities currently exist for remote monitoring.

# Feasibility Study Scope

Suppliers must determine how best to interface the lift “Lift Out of Service” outputs available on different lifts across the LU & DLR to develop a data feed which can be integrated into TfL systems in order to fulfil the project objectives previously stated.

## Critical Issues Identified

Nearly all lifts in scope provide outputs to confirm whether a lift is in operation or not. This information is accessed only by operational staff in the Station Operations Room of the station in which the lift operates, or in the case of the DLR, staff in a central control centre. The purpose of this monitoring is to notify operational staff of a lift breakdown as soon as it occurs so that the lift maintainers can be instructed to attend without delay.

In some surface locations there will be easy access to the extant lift signals in the Station Operations Room. However, in sub-surface stations where the lifts and the Station Operations Room are located below ground, access may be more difficult. TfL are looking for innovative solutions that will overcome these issues with minimal cost & disturbance to existing infrastructure.

A status output is available from most lifts in scope. There is no one single method of providing theses outputs and various different types of monitoring & computerised station Management Systems are in use. The differing means of reporting status are shown in Appendix A.

3.2 Research & Analysis of Existing Systems and Operations

3.2.1 		Lifts monitored in station

The outputs in use are either: integrated with a Station Management System, report to a discrete hardwired indicator panel or report to a central monitoring system as described below.

In all cases outputs from the lift controller confirm:

I.	Lift failure

II.	Lift power failure

III.	Operation of the emergency passenger alarm

3.2.1.1	Integrated with proprietary Station Management System (SMS)

These systems are for management of all station assets including lifts. The SMS operational user Visual Display Unit is situated in the Station Operations Room (SOR).

In some stations the lifts may be integrated with a station wide communications system which gives the option to connect to the Local Area Network. The LAN uses Ethernet protocol to integrate with the SMS. The communication systems are all manufactured by Commend and are of the GE700 or GE800 type. Typical LAN connections are shown in Appendix C.

3.2.1.2.	Non-integrated - Lift Status Panel

Where a compatible SMS is not available the lift may report to a discrete Lift Status Panel situated in the Station Operations Room (SOR) which provides an audio-visual display of lift status.

In both the above cases the lift controller outputs are connected to the monitoring facility in the lift machine room or in the Lift Electrical Equipment Room (LEER).

3.2.2. 	Lifts remotely monitored

Lifts on the DLR network take outputs from the lifts to report status to a central Station Management System located at Becton Control Centre. Lift monitoring is managed by the CMC-Anywhere system provided by Thames Valley Controls Ltd.

3.2.3.	No lift status output

Some older lifts have no facility for station or remote monitoring. See Appendix A

## Physical Environment

The lifts in scope are all located in station environments. Some are surface locations where the lifts & the SOR are above ground, others are sub-surface where the lifts and SOR are below ground.

## Site Surveys

Suppliers may find it necessary to undertake site surveys depending on the remote data acquisition method proposed.

## Other Assumptions & Constraints

Any product selected for trial via the MSQ process must not impact on any existing operational systems i.e. Status indication will be unaffected by the integration.

# APPENDIX A – Lifts in Scope

# *PMVT – Primary Means of Vertical Transport (the main mode of transport from street to platform)

*SMVT - Secondary Means of Vertical Transport (lifts which supplement stairs or escalators and are used principally to provide step free access)

| Network | Lift | Asset number | PMVT | SMVT | Status Monitoring Method |
| --- | --- | --- | --- | --- | --- |
| LU | Acton Town 01 | D205-L01 | No | Yes | Station SMS / Status Panel |
| LU | Acton Town 02 | D205-L02 | No | Yes | Station SMS / Status Panel |
| LU | Bank 02 | N133-L02 | Yes | No | Station SMS / Status Panel |
| LU | Bank 03 | N133-L03 | Yes | No | Station SMS / Status Panel |
| LU | Bank 04 | N133-L04 | Yes | No | Station SMS / Status Panel |
| LU | Bank 05 | N133-L05 | Yes | No | Station SMS / Status Panel |
| LU | Bank 06 | N133-L06 | No | Yes | Station SMS / Status Panel |
| LU | Bank 07 | N133-L07 | No | Yes | Station SMS / Status Panel |
| LU | Bank 08 | N133-L08 | No | Yes | Station SMS / Status Panel |
| LU | Bank 09 | N133-L09 | No | Yes | Station SMS / Status Panel |
| LU | Belsize Park 02 | N045-L02 | Yes | No | Station SMS |
| LU | Belsize Park 03 | N045-L03 | Yes | No | Station SMS |
| LU | Belsize Park 04 | N045-L04 | Yes | No | Station SMS |
| LU | Bermondsey 01 | J011-L01 | No | Yes | Station SMS / Status Panel |
| LU | Blackfriars 06 | D091-L06 | No | Yes | Station SMS / Status Panel |
| LU | Blackfriars 08 | D091-L08 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 01 | C125-L01 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 02 | C125-L02 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 03 | C125-L03 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 04 | C125-L04 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 05 | C125-L05 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 06 | C125-L06 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 07 | C125-L07 | No | Yes | Station SMS / Status Panel |
| LU | Bond Street 08 | C125-L08 | No | Yes | Station SMS / Status Panel |
| LU | Borough 01 | N137-L01 | Yes | No | Station SMS |
| LU | Borough 02 | N137-L02 | Yes | No | Station SMS |
| LU | Brixton 01 | V059-L01 | No | Yes | Station SMS |
| LU | Brixton 02 | V059-L02 | No | Yes | Station SMS |
| LU | Bromley-by-Bow 01 | D043-L01 | No | Yes | Station SMS / Status Panel |
| LU | Bromley-by-Bow 02 | D043-L02 | No | Yes | Station SMS / Status Panel |
| LU | Caledonian Road 03 | P047-L03 | Yes | No | Station SMS |
| LU | Caledonian Road 04 | P047-L04 | Yes | No | Station SMS |
| LU | Canada Water 01 | J009-L01 | No | Yes | Station SMS / Status Panel |
| LU | Canada Water 02 | J009-L02 | No | Yes | Station SMS / Status Panel |
| LU | Canada Water 04 | J009-L04 | No | Yes | Station SMS / Status Panel |
| LU | Canary Wharf 01 | J007-L01 | No | Yes | Station SMS / Status Panel |
| LU | Canary Wharf 02 | J007-L02 | No | Yes | Station SMS / Status Panel |
| LU | Canning Town 01 | J003-L01 | No | Yes | Station SMS / Status Panel |
| LU | Canning Town 02 | J003-L02 | No | Yes | Station SMS / Status Panel |
| LU | Canning Town 03 | J003-L03 | No | Yes | Station SMS / Status Panel |
| LU | Cannon Street 01 | D083-L01 | No | Yes | Station SMS / Status Panel |
| LU | Cannon Street 02 | D083-L02 | No | Yes | Station SMS / Status Panel |
| LU | Chalk Farm 01 | N047-L01 | Yes | No | Station SMS |
| LU | Chalk Farm 02 | N047-L02 | Yes | No | Station SMS |
| LU | Covent Garden 01 | P057-L01 | Yes | No | Station SMS |
| LU | Covent Garden 02 | P057-L02 | Yes | No | Station SMS |
| LU | Covent Garden 03 | P057-L03 | Yes | No | Station SMS |
| LU | Covent Garden 04 | P057-L04 | Yes | No | Station SMS |
| LU | Earl's Court 03 | P077-L03 | Yes | No | Station SMS / Status Panel |
| LU | Earl's Court 04 | P077-L04 | Yes | No | Station SMS / Status Panel |
| LU | Earl's Court 05 | P077-L05 | No | Yes | Station SMS / Status Panel |
| LU | Earl's Court 06 | P077-L06 | No | Yes | Station SMS / Status Panel |
| LU | East Ham 01 | D033-L01 | No | Yes | Station SMS / Status Panel |
| LU | East Ham 02 | D033-L02 | No | Yes | Station SMS / Status Panel |
| LU | Edgware 01 | N021-L01 | No | Yes | Station SMS / Status Panel |
| LU | Edgware 02 | N021-L02 | No | Yes | Station SMS / Status Panel |
| LU | Edgware Road (Bak) 01 | B073-L01 | Yes | No | Station SMS |
| LU | Edgware Road (Bak) 02 | B073-L02 | Yes | No | Station SMS |
| LU | Elephant & Castle 01 | N139-L01 | Yes | No | Station SMS |
| LU | Elephant & Castle 03 | N139-L03 | Yes | No | Station SMS |
| LU | Elephant & Castle 04 | N139-L04 | Yes | No | Station SMS |
| LU | Elephant & Castle 05 | N139-L05 | Yes | No | Station SMS |
| LU | Elephant & Castle 06 | N139-L06 | Yes | No | Station SMS |
| LU | Euston Square 01 | M117-L01 | No | Yes | Station SMS / Status Panel |
| LU | Euston Square 02 | M117-L02 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 01 | M123-L01 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 02 | M123-L02 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 03 | M123-L03 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 04 | M123-L04 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 05 | M123-L05 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 06 | M123-L06 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 07 | M123-L07 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 08 | M123-L08 | No | Yes | Station SMS / Status Panel |
| LU | Farringdon 09 | M123-L09 | No | Yes | Station SMS / Status Panel |
| LU | Finchley Central 01 | N071-L01 | No | Yes | Station SMS / Status Panel |
| LU | Finchley Central 02 | N071-L02 | No | Yes | Station SMS / Status Panel |
| LU | Finsbury Park 01 | P041-L01 | No | Yes | Station SMS / Status Panel |
| LU | Finsbury Park 03 | P041-L03 | No | Yes | Station SMS / Status Panel |
| LU | Fulham Broadway 01 | D153-L01 | No | Yes | Station SMS / Status Panel |
| LU | Fulham Broadway 02 | D153-L02 | No | Yes | Station SMS / Status Panel |
| LU | Gloucester Road 03 | P075-L03 | Yes | No | Station SMS |
| LU | Gloucester Road 04 | P075-L04 | Yes | No | Station SMS |
| LU | Golders Green 01 | N041-L01 | No | Yes | Station SMS / Status Panel |
| LU | Golders Green 02 | N041-L02 | No | Yes | Station SMS / Status Panel |
| LU | Goodge Street 01 | N103-L01 | Yes | No | Station SMS |
| LU | Goodge Street 02 | N103-L02 | Yes | No | Station SMS |
| LU | Goodge Street 03 | N103-L03 | Yes | No | Station SMS |
| LU | Goodge Street 04 | N103-L04 | Yes | No | Station SMS |
| LU | Green Park 01 | P065-L01 | No | Yes | Station SMS / Status Panel |
| LU | Green Park 02 | P065-L02 | No | Yes | Station SMS / Status Panel |
| LU | Green Park 04 | P065-L04 | No | Yes | Station SMS / Status Panel |
| LU | Green Park 05 | P065-L05 | No | Yes | Station SMS / Status Panel |
| LU | Green Park 06 | P065-L06 | No | Yes | Station SMS / Status Panel |
| LU | Greenford 01 | C157-L01 | No | Yes | Station SMS / Status Panel |
| LU | Hainault 01 | C059-L01 | No | Yes | Station SMS / Status Panel |
| LU | Hainault 02 | C059-L02 | No | Yes | Station SMS / Status Panel |
| LU | Hainault 03 | C059-L03 | No | Yes | Station SMS / Status Panel |
| LU | Hammersmith (D&P) 01 | D177-L01 | No | Yes | Station SMS / Status Panel |
| LU | Hammersmith (D&P) 02 | D177-L02 | No | Yes | Station SMS / Status Panel |
| LU | Hammersmith Bus Station 09 | X170-L09 | No | Yes | Station SMS / Status Panel |
| LU | Hammersmith Bus Station 10 | X170-L10 | No | Yes | Station SMS / Status Panel |
| LU | Hampstead 01 | N043-L01 | Yes | No | Station SMS |
| LU | Hampstead 02 | N043-L02 | Yes | No | Station SMS |
| LU | Hampstead 03 | N043-L03 | Yes | No | Station SMS |
| LU | Hampstead 04 | N043-L04 | Yes | No | Station SMS |
| LU | Heathrow Terminals 2,3 01 | D233-L01 | No | Yes | Station SMS / Status Panel |
| LU | Heathrow Terminals 2,3 02 | D233-L02 | No | Yes | Station SMS / Status Panel |
| LU | Hendon Central 01 | N031-L01 | No | Yes | Station SMS / Status Panel |
| LU | Hillingdon 01 | P115-L01 | No | Yes | Station SMS / Status Panel |
| LU | Hillingdon 02 | P115-L02 | No | Yes | Station SMS / Status Panel |
| LU | Holland Park 01 | C137-L01 | Yes | No | Station SMS |
| LU | Holland Park 02 | C137-L02 | Yes | No | Station SMS |
| LU | Holloway Road 01 | P045-L01 | Yes | No | None |
| LU | Holloway Road 02 | P045-L02 | Yes | No | None |
| LU | Hounslow East 01 | D223-L01 | No | Yes | Station SMS / Status Panel |
| LU | Hounslow East 02 | D223-L02 | No | Yes | Station SMS / Status Panel |
| LU | Kennington 01 | N143-L01 | Yes | No | None |
| LU | Kennington 02 | N143-L02 | Yes | No | None |
| LU | Kilburn 01 | B103-L01 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 01 | N123-L01 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 02 | N123-L02 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 03 | N123-L03 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 05 | N123-L05 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 06 | N123-L06 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 07 | N123-L07 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 08 | N123-L08 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 10 | N123-L10 | No | Yes | Station SMS / Status Panel |
| LU | King's Cross 11 | N123-L11 | No | Yes | Station SMS / Status Panel |
| LU | Kingsbury 01 | B087-L01 | No | Yes | Station SMS / Status Panel |
| LU | Kingsbury 02 | B087-L02 | No | Yes | Station SMS / Status Panel |
| LU | Lambeth North 01 | B137-L01 | Yes | No | Station SMS |
| LU | Lambeth North 02 | B137-L02 | Yes | No | Station SMS |
| LU | Lancaster Gate 01 | C129-L01 | Yes | No | Station SMS |
| LU | Lancaster Gate 02 | C129-L02 | Yes | No | Station SMS |
| LU | Liverpool Street 01 | C101-L01 | No | Yes | Station SMS / Status Panel |
| LU | Liverpool Street 02 | C101-L02 | No | Yes | Station SMS / Status Panel |
| LU | Liverpool Street 03 | C101-L03 | No | Yes | Station SMS / Status Panel |
| LU | Liverpool Street 05 | C101-L05 | No | Yes | Station SMS / Status Panel |
| LU | Liverpool Street 06 | C101-L06 | No | Yes | Station SMS / Status Panel |
| LU | Liverpool Street 07 | C101-L07 | No | Yes | Station SMS / Status Panel |
| LU | Liverpool Street 08 | C101-L08 | No | Yes | Station SMS / Status Panel |
| LU | Liverpool Street 09 | C101-L09 | No | Yes | Station SMS / Status Panel |
| LU | London Bridge 02 | N135-L02 | No | Yes | Station SMS / Status Panel |
| LU | London Bridge 03 | N135-L03 | No | Yes | Station SMS / Status Panel |
| LU | London Bridge 04 | N135-L04 | No | Yes | Station SMS / Status Panel |
| LU | Morden 01 | N177-L01 | No | Yes | Station SMS / Status Panel |
| LU | Morden 02 | N177-L02 | No | Yes | Station SMS / Status Panel |
| LU | Mornington Crescent 01 | N093-L01 | Yes | No | None |
| LU | Mornington Crescent 02 | N093-L02 | Yes | No | None |
| LU | Newbury Park 01 | C067-L01 | No | Yes | Station SMS / Status Panel |
| LU | Newbury Park 02 | C067-L02 | No | Yes | Station SMS / Status Panel |
| LU | North Greenwich 01 | J005-L01 | No | Yes | Station SMS / Status Panel |
| LU | North Greenwich 02 | J005-L02 | No | Yes | Station SMS / Status Panel |
| LU | North Greenwich 04 | J005-L04 | No | Yes | Station SMS / Status Panel |
| LU | Oakwood 01 | P013-L01 | No | Yes | Station SMS / Status Panel |
| LU | Paddington 01 |  | No | Yes | Station SMS / Status Panel |
| LU | Paddington 03 | B071-L03 | No | Yes | Station SMS / Status Panel |
| LU | Pinner 01 | M071-L01 | No | Yes | Station SMS / Status Panel |
| LU | Pinner 02 | M071-L02 | No | Yes | Station SMS / Status Panel |
| LU | Queensway 01 | C133-L01 | Yes | No | Station SMS |
| LU | Queensway 02 | C133-L02 | Yes | No | Station SMS |
| LU | Regent's Park 01 | B123-L01 | Yes | No | None |
| LU | Regent's Park 02 | B123-L02 | Yes | No | None |
| LU | Russell Square 01 | P053-L01 | Yes | No | Station SMS / Status Panel |
| LU | Russell Square 02 | P053-L02 | Yes | No | Station SMS / Status Panel |
| LU | Russell Square 03 | P053-L03 | Yes | No | Station SMS / Status Panel |
| LU | Southfields 01 | D165-L01 | No | Yes | Station SMS / Status Panel |
| LU | Southwark 01 | J013-L01 | No | Yes | Station SMS / Status Panel |
| LU | Southwark 02 | J013-L02 | No | Yes | Station SMS / Status Panel |
| LU | Stratford 04 | C091-L04 | No | Yes | Station SMS / Status Panel |
| LU | Stratford 05 | C091-L05 | No | Yes | Station SMS / Status Panel |
| LU | Stratford 06 | C091-L06 | No | Yes | Station SMS / Status Panel |
| LU | Stratford 07 | C091-L07 | No | Yes | Station SMS / Status Panel |
| LU | Stratford 08 | C091-L08 | No | Yes | Station SMS / Status Panel |
| LU | Stratford 16 | C091-L16 | No | Yes | Station SMS / Status Panel |
| LU | Stratford 17 | C091-L17 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 01 | N105-L01 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 02 | N105-L02 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 03 | N105-L03 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 04 | N105-L04 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 05 | N105-L05 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 07 | N105-L07 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 08 | N105-L08 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 09 | N105-L09 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 10 | N105-L10 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 11 | N105-L11 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Court Road 12 | N105-L12 | No | Yes | Station SMS / Status Panel |
| LU | Tottenham Hale 01 | V025-L01 | No | Yes | Station SMS / Status Panel |
| LU | Tower Hill 01 | D077-L01 | No | Yes | Station SMS / Status Panel |
| LU | Tower Hill 02 | D077-L02 | No | Yes | Station SMS / Status Panel |
| LU | Tufnell Park 01 | N083-L01 | Yes | No | Station SMS |
| LU | Tufnell Park 02 | N083-L02 | Yes | No | Station SMS |
| LU | Vauxhall 01 | X168-L01 | No | Yes | Station SMS / Status Panel |
| LU | Vauxhall 02 | V055-L02 | No | Yes | Station SMS / Status Panel |
| LU | Victoria 01 | V047-L01 | No | Yes | Station SMS / Status Panel |
| LU | Victoria 02 | V047-L02 | No | Yes | Station SMS / Status Panel |
| LU | Victoria 03 | V047-L03 | No | Yes | Station SMS / Status Panel |
| LU | Victoria 04 | V047-L04 | No | Yes | Station SMS / Status Panel |
| LU | Victoria 05 | V047-L05 | No | Yes | Station SMS / Status Panel |
| LU | Victoria 06 | V047-L06 | No | Yes | Station SMS / Status Panel |
| LU | Victoria 07 | V047-L07 | No | Yes | Station SMS / Status Panel |
| LU | Walthamstow Central 01 | V021-L01 | No | Yes | Station SMS / Status Panel |
| LU | Walthamstow Central 02 | V021-L02 | No | Yes | Station SMS / Status Panel |
| LU | Waterloo 02 | N115-L02 | No | Yes | Station SMS / Status Panel |
| LU | Waterloo 04 | N115-L04 | No | Yes | Station SMS / Status Panel |
| LU | Wembley Park 01 | B091-L01 | No | Yes | Station SMS / Status Panel |
| LU | Wembley Park 02 | B091-L02 | No | Yes | Station SMS / Status Panel |
| LU | Wembley Park 03 | B091-L03 | No | Yes | Station SMS / Status Panel |
| LU | Wembley Park 04 | B091-L04 | No | Yes | Station SMS / Status Panel |
| LU | Wembley Park 05 | B091-L05 | No | Yes | Station SMS / Status Panel |
| LU | West Ham 01 | D039-L01 | No | Yes | Station SMS / Status Panel |
| LU | West Ham 02 | D039-L02 | No | Yes | Station SMS / Status Panel |
| LU | West Ham 04 | D039-L04 | No | Yes | Station SMS / Status Panel |
| LU | Westminster 02 | D101-L02 | No | Yes | Station SMS / Status Panel |
| LU | Westminster 03 | D101-L03 | No | Yes | Station SMS / Status Panel |
| LU | Westminster 04 | D101-L04 | No | Yes | Station SMS / Status Panel |
| LU | Westminster 05 | D101-L05 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 01 | D061-L01 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 02 | D061-L02 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 03 | D061-L03 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 04 | D061-L04 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 05 | D061-L05 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 06 | D061-L06 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 07 | D061-L07 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 08 | D061-L08 | No | Yes | Station SMS / Status Panel |
| LU | Whitechapel 10 | D061-L10 | No | Yes | Station SMS / Status Panel |
| LU | Wood Lane 01 | M183-L01 | No | Yes | Station SMS / Status Panel |
| LU | Wood Lane 02 | M183-L02 | No | Yes | Station SMS / Status Panel |
| LU | Wood Lane 03 | M183-L03 | No | Yes | Station SMS / Status Panel |
| LU | Wood Lane 04 | M183-L04 | No | Yes | Station SMS / Status Panel |
| LU | Cockfosters | L1 | No | Yes | Station SMS |
| LU | Mill Hill East | L1 | No | Yes | Station SMS |
| LU | Osterley | L2 | No | Yes | Station SMS |
| LU | Osterley | L1 | No | Yes | Station SMS |
| LU | Harrow on the Hill | L1 | No | Yes | Station SMS |
| LU | Harrow on the Hill | L2 | No | Yes | Station SMS |
| LU | Harrow on the Hill | L3 | No | Yes | Station SMS |
| LU | Harrow on the Hill | L4 | No | Yes | Station SMS |
| LU | Amersham | L1 | No | Yes | Station SMS |
| LU | Amersham | L2 | No | Yes | Station SMS |
| LU | Burnt Oak (On Hold) | L1 | No | Yes | Station SMS |
| LU | Debden | L2 | No | Yes | Station SMS |
| LU | Debden | L1 | No | Yes | Station SMS |
| LU | Hanger Lane (On Hold) | L1 | No | Yes | Station SMS |
| LU | Ickenham | L2 | No | Yes | Station SMS |
| LU | Ickenham | L1 | No | Yes | Station SMS |
| LU | Leyton | L2 | No | Yes | Station SMS |
| LU | Leyton | L1 | No | Yes | Station SMS |
| LU | Northolt (On Hold) | L1 | No | Yes | Station SMS |
| LU | Sudbury Hill | L2 | No | Yes | Station SMS |
| LU | Sudbury Hill | L1 | No | Yes | Station SMS |
| LU | Wimbledon Park | L1 | No | Yes | Station SMS |
| DLR | East India 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | East India 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | East India 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | Limehouse 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | Limehouse 04 | Lift 4 | No | Yes | Control Centre SMS |
| DLR | Prince Regent 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Poplar 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Poplar 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Royal Victoria 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Royal Victoria 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Royal Victoria 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | Galleon's Reach 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Galleon's Reach 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | West ferry 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | West ferry 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Blackwall 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Blackwall 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Devons Road 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Devons Road 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Royal Albert 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Royal Albert 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Bow church 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Bow church 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | West India Quay 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | West India Quay 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Cross Harbour 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Cross Harbour 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Custom House 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | All Saints 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | All Saints 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Heron Quay 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Heron Quay 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | London City Airport 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | London City Airport 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Pontoon Dock 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Pontoon Dock 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | West Silver Town 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | West Silver Town 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | King George V 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | King George V 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Langdon Park 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Langdon Park 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Custom House 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | Limehouse 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Limehouse 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Prince Regent 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | South Quay 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | South Quay 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | West ferry 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | West ferry 04 | Lift 4 | No | Yes | Control Centre SMS |
| DLR | Woolwich Arsenal 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Woolwich Arsenal 02 | Lift 2 Intervention Shaft | No | Yes | Control Centre SMS |
| DLR | Woolwich Arsenal 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | Woolwich Arsenal 04 | Lift 4 | No | Yes | Control Centre SMS |
| DLR | Abbey Road 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Abbey Road 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Canning Town 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Star Lane 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Star Lane 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Star Lane 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | Stratford High Street 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Stratford High Street 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Stratford International 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Stratford International 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Stratford International 03 | Lift 3 | No | Yes | Control Centre SMS |
| DLR | West Ham 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Prince regent 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Tower Gateway 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Tower Gateway 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Pudding Mill Lane 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Pudding Mill Lane 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Poplar 03 | Lift 3 HLW | No | Yes | Control Centre SMS |
| DLR | Poplar 04 | Lift 4 HLW | No | Yes | Control Centre SMS |
| DLR | Canary Wharf 01 | Lift 1 | No | Yes | Control Centre SMS |
| DLR | Canary Wharf 02 | Lift 2 | No | Yes | Control Centre SMS |
| DLR | Shadwell 01 | Lift 1 | No | Yes | Control Centre SMS |

# APPENDIX B - Lift Status Panel – images & typical circuit diagram

# APPENDIX C – Typical LAN connections