## APPENDIX A - SPECIFICATION

SHEPWAY DISTRICT COUNCIL

Project Title: Installation of Fire Detection System

& Fire Alarm to the Civic Centre

Reference Number: A7TH-GHS11K

# APPENDIX A  - SPECIFICATION

| ACTIVITY |
| --- |
| Principal Objectives |
| 1.1 | The principal objective of the work is to provide a new Fire Detection & Alarm System to the Civic Centre, Castle Hill Avenue, Folkestone, Kent, CT20 2QY. The Civic Centre comprises a nine storey tower block, basement, with first and second floor extensions and ground floor low rise accommodation situated in central Folkestone. The contract will be let on JCT 2011 Minor Works Building Contract. |
| Risks and insurance |
| 2.1 | The minimum limit of indemnity for insurance in respect of loss of or damage to property (except the works, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) caused by activity in connection with this contract for any one event is £5,000,000. The policy is to have excess sums of no more than £5,000 per incident or series of incidents. |
| 2.2 | The minimum limit of indemnity for insurance in respect of death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract for any one event is £10,000,000. The policy is to have excess sums of no more than £5,000 per incident or series of incidents. |
| 2.3 | The minimum limit of indemnity for insurance in respect of any liability for damage or compensation arising out of any neglect, error, omission or failure committed or alleged to have been committed in rendering any professional advice and/or services (Professional Indemnity) in connection with this contract for any one event is £5,000,000. The policy is to have excess sums of no more than £5,000 per incident or series of incidents. |
| 2.4 | The Contractor is liable to the Council for loss or damage to the Employer’s property. |
| 2.5 | Contractors must submit with their quotations details of the terms of the insurance they propose to effect, or which they already hold and intend to use, to meet the requirements of the above three clauses. |
| Health and Safety |
| 3.1 | The Contractor shall adopt safe methods of work and comply with all other requirements of the Health and Safety at Work etc Act 1974, and the CDM Regulations 2015 in order to protect the health and safety of its personnel, Council employees, patrons and visitors to each location. |
| 3.2 | The Contractor will be required to undertake a risk assessment and develop method statements for all significant risks identified. The method statements shall include information on the major items of plant and construction methods to be used. The method statements are to be approved by the Council prior to the works commencing. |
| 3.3 | There are no facilities at the site for offices, messing, sanitary and welfare facilities, storage, parking, power, water or telecommunications. The Contractor shall forward information to the Council at least one week prior to the works commencing, detailing his proposals and shall include here any costs for provision of any temporary facilities as may be required. |
| Hazardous Substances |
| 4.1 | When substances covered by the Control of Substances Hazardous to Health (COSHH) Regulations are likely to be encountered or used by the Contractor, the Contractor shall maintain Health Risk Assessment Statements relevant to any of his activities on the site which may be affected by the substances. The Contractor shall hold on site relevant Product Hazard Sheets and evidence of the control, exposure monitoring and health surveillance measures to be employed. |
| 4.2 | Records of examinations and tests carried out shall be available at all times for inspection by the Council and the HSE. |
| 4.3 | The Contractor shall warn and instruct his workmen and all other persons (including sub-contractors' workmen and visitors) under his control as to the hazards and precautions to be taken. Such instruction shall be documented in the Construction Phase Health and Safety Plan. |
| 4.4 | The Contractor shall remain alert to the possibility that other hazards may exist which are not identified prior to work commencing. |
| 4.5 | The Contractor shall establish a procedure to ensure that all persons requiring instruction or warning actually receive and understand the instruction or warning, together with a record thereof. He shall furnish such records to the Council when called upon to do so. |
| Working Hours |
| 5.0 | Access to the Civic Centre is required during normal opening times Monday to Friday. Should there be any reason during the duration of the works to restrict or curtail normal access the Contractor shall include in his price for undertaking all or part of the works during weekend working and in accordance with the Council’s Construction Works Policy. Note: Sunday working will be permitted, contrary to information given in the Construction Works Policy. If the works need to be programmed over consecutive weekends, then allow for temporary warning signage to be installed and maintained. |
| Supervision |
| 6.0 | The Contractor is to ensure that a suitably qualified and experienced foreman (or equivalent) is on site during all working hours to direct work activities including plant and personnel. The foreman shall ensure that the works are carried out safely and efficiently. |
| Security |
| 7.1 | Security at the site is entirely the Contractor’s responsibility. The Contractor is to provide and maintain suitable security measures throughout the period of the works. |
| 7.2 | When parked overnight, all plant is to be covered and/or protected in an appropriate manner to ensure any possible vandalism is kept to a minimum (e.g. all fuel filler points must be secured, windscreens must be shielded etc). |
| Access to site |
| 8.1 | Access to the site will be via Palting Way, which is the quieter approach, to the rear staff car park. Arrangements for parking will be made for contractors for the duration of the works. Care should be exercised at all times in approaching the site and particularly in operations where the loading and unloading of plant and equipment will be necessary. |
| 8.2 | On no account shall the Contractor prevent or obstruct access to any property, unless unavoidable for safety or other reasons and only with the permission of the Council. |
| The Works |
| 9.1 | To supply, deliver, install and commission an addressable Fire Detection and Fire Alarm system for the Civic Centre; which comprises a nine storey tower block, basement, extensions to the first and second floors with ground floor additions. The installation shall be compliant with BS 5839 Part 1: 2013 Category L1 and Part M of the Building Regulations. Training on use of the system shall be provided by the winning contractor immediately following successful commissioning of the system. The contractor shall: • Undertake and Project Manage the Fire Detection & Fire Alarm Electrical Installation & Cabling (Standard Category) • Supply the Manual Detection Devices (Break Glass Call Points) • Supply the Automatic Detection Devices (Optical Smoke Detectors, Heat Detectors) • Supply the Audible Alarm Devices • Supply the Visual Alarm Devices • Remove & Blank off existing equipment including decommisioning and isolating the old system once new system is operational • Arrange System Commissioning and Testing • Organise System Demonstration & Training for the client • Record Drawings and Operation & Maintenance Documentation and supply to the client upon completion |
|  | When quoting for this contractors should have regard to the following: The existing wiring installation is to be removed along with redundant devices, where devices have been removed blanking plates are to be installed; Contractors should provide a price for the removal of any Ionisation detectors that may be identified on a per item basis; Wiring should be standard fire rated PH 30, unless otherwise specified, see below; Contractors should price for a two panels in separate locations, if required to minimise the cabling required in the main riser to the Tower, which shall be networked. Cabling to network the panels should be to the enhanced PH120 fire rated standard. The system must interface with automatic gas shut off valve, be networked and link into the door access systems and the AOV system. Audible Alarm Devices should achieve an Audible alarm of 65db(A) throughout the building, unless the room is less than 60m2 where 60 db(A) should be achieved. Visual Alarm Devices should be installed in toilets throughout the building to ensure compliance with the requirements of BS5839 Part 1: 2013 Clause 17 and manufactured in accordance with BS EN 54 Part 23 2010. Contractors should ensure that the installation achieves compliance with Part M of the Building Regulations, Schedule 1 in this regard. These devices shall be non addressable. Manual Call Points should be installed at all exits to open air from the building, on all storey exits (stair lobbies) and escape routes so that no one should travel more than 45 metres to a call point. Working Hours It is anticipated that the majority of the works will be able to be completed during normal working hours, however, contractors should provide a contingency sum for some out of hours working. |
|  | Main Control Equipment Should include, but not limited in its extent to the following specification: • Supports intelligent/programmable remote terminals • Approved to EN54 parts 2 & 4 • Support 8 detection loops, each supporting the capacity for control and monitoring of multiple devices • Optional peripherial expansion capability • Select and click programming • Must be compatible with industry standard protocols such as, Apollo Discovery, Argus Vega, Hochiki ESP and Nittan Evolution • Single area false alarm management • Built in voltage and current meters The installation should be of an open protocol, non proprietary system. Contractors shall provide as installed drawings, following installation. Devices shall all be hard wired, unless agreed with the client. A contingency sum should be included for wireless devices where hard wiring is not achievable. Areas of increased risk: Contractors should give due cognisance to the following areas when designing the installation: • Plant Room & Lift Room 9th floor • Boiler room, switch room main electrical riser. All contractors are required to visit site prior to the submission of their quotation. Contractors should provide an Annual Maintenance per annum and include a price for attendance in normal business hours and out of hours should there be a system failure. |
| 9.2 | The Contractor shall take all necessary precautions to avoid damaging all land and property, including highways, adjacent areas within the car park and access ways, buildings, boundary walls, fences, structures, grassed areas, plants etc. |
| 9.3 | On or before completion he shall make good any damage caused, including by sub-contractors and suppliers, and clean away any debris at his own expense, to the satisfaction of the Council. Making good shall be with identical and matching materials or the complete item(s) shall be replaced with approved alternative materials |
| 9.4 | The Council’s opinion regarding original condition shall be final. |
| Plant and Equipment |
| 10.1 | The Contractor is to supply all necessary plant and equipment to ensure the safe and efficient completion of the works and is to allow for all necessary associated work including fuelling, maintenance and cleaning. |
| 10.2 | Copies of all personnel certification/machine tickets must be provided by the Contractor prior to the works commencing. |
| 10.3 | Copies of all risk assessments and method statements must be provided by the Contractor prior to the works commencing. |
| 10.4 | The Contractor shall choose appropriate plant and use best practice to minimise the amount of noise and vibration during working hours. |
| 10.5 | In the event that Shepway District Council require further works we request that the price for repair is detailed on a price per metre basis. |