SCHEDULE OF WORKS

Carry out the following checks and inspections in accordance with the HSE’s Approved Code of Practice (ACOP) L8.

Details for each site are enclosed on the attached site checklist. The scope of the works will vary between each site, but will include the following.

- Monthly temperature testing of both hot and cold tap outlets which involves running each tap for two minutes, monitoring and recording the temperature(s).

- The results of the monthly tests need only be electronically forwarded to the Contract Administrator every three months, on the check sheets provided, unless a situation is found that requires immediate action by the Contract Administrator. For example if an outlet temperature falls outside the permitted range as specified by the ACOP (Hot < 55deg C; Cold > 20 deg C).

- Bi-annual visual inspection of cold water storage tanks, and carrying out any remedial works after discussion with the Contract Administrator.

- Annual bacteriological testing of the cold water storage tanks. The samples should be collected in accordance with ISO 11731:1998; with samples being tested by an UKAS accredited laboratory that takes part in the Public Health Laboratory Service Water Microbiology External Quality Assessment Scheme for the isolation of Legionella.

- Annual disinfection of the hot and cold water systems, again in accordance with HSE ACOP L8.

- Quarterly dismantling and cleaning of shower heads (where applicable).

- If during the conduct of the testing, any fault is discovered it should be immediately reported to the Contract Administrator, along with an estimate based on daywork rates for the repair of the said fault. Repair work to be carried out at the discretion of the Contract Administrator.