Lot 2 Fire doors

Bristol City Council (BCC) is currently replacing over 1000 fire door sets per year with the doors and joinery being produced by our own joinery workshop and installed by the in-house workforce. However they do not currently have capacity to meet all our programme requirements. Therefore BCC intends to enter into a 4 year DPS Contract starting April 2020 with approved contractors to meet our programme requirements. The contract will be for;

Fit only FD30s or FD60s fire doors and frames supplied by BCC,

Or Supply and fit new FD30s or FD60s fire doors and frames (low volumes only)

Or supply and fit new timber framed glazed fire screens (low volumes only),

Or maintenance & repair of fire doors.

Or supply and fit fire resistant meter cupboard doors (low volumes only).

Primarily the work will be to low-rise flats and maisonettes. This contract involves carrying out replacing existing doors and frames to occupied residential flats and communal areas to blocks of between 2 & 5 storeys high blocks with various tenures. In addition some work may be required to be carried out in our high-rise blocks. The value of the work is estimated to be between £0 and £200,000 per year with individual contracts ranging from £5,000 to £100,000 depending on the package of work. Where possible packages will be made up of blocks of flats in close proximity to each other.

BCC seeks the services of a specialist BM TRADA Q-Mark Fire Door Installation scheme certified (or equivalent where the accreditation is with the company, supervisors and operatives) accredited contractor who is well resourced and experienced in this type of specialist fire door installation and maintenance work. The successful contractor will be invited to provide evidence of its accreditation with TRADA and any other relevant bodies, demonstrate it has undertaken a project of a similar nature in the recent past and is fully up to date with current legislation and practice, as well as the usual compliances such as ISO 9002, adequate insurances, CSCS cards and CRB/DBS checks for site operatives.

Doors sets

Where the request is for the supply and fit of a fire door set the contractor is to supply door sets that meet the requirements stated. The door, frame and all ironmongery, closer, fittings, intumescent pads, strips and seals are to meet the requirements and constraints of the Global Assessment and testing for the door blank being provided. BCC are currently using Sainty (Sentry door) door blanks under the most recent updated Global assessment. The ironmongery spec below meets the requirements and constraints of the Sainty Global assessment. The contractor will be expected to supply the same Sainty doors or an exact match. If the contractor wishes to offer an alternative door set, the contractor will be expected to provide a copy of the Global Assessment for the door being used. Ideally the Global assessment will include the exact same ironmongery, fittings, intumescent pads etc. listed below. The contractor will be expected to provide samples of the door, ironmongery, closer, fittings and intumescent pads for approval before starting works on site. All works carried out to the door and materials used (lipping, glues, pins, screws etc.) on or off site are to be in line with the requirements and constraints of the Global Assessment. The contractor will provide suitable fixings, fire retardant packing & intumescent sealants to seal between the frame and the structural openings, architraves and cover beads/ mouldings, brass numerals as required. Where doors or storey frames require glazing the glass is to be fire rated glass suitable for the location bedded in intumescent strips held in place with suitable glazing beads. The Contractor will be responsible for all on site measurements prior to the ordering/ manufacture of the door set.

Where the request is for the fit only of a fire door set the contractor will be provided with a door, frame, ironmongery pack, closer, intumescent pads, strips & seals via the BCC joinery workshop. The contractor will provide suitable fixings, fire retardant packing & intumescent sealants to seal between the frame and the structural openings, architraves and cover beads/ mouldings, brass numerals as required. The contract will be required to arrange for the collection and transportation of door sets & ironmongery packs from the Joinery workshop located at Wellington Rd, St Pauls Bristol. BS2 9ER or from Sandy Park Road, Brislington, Bristol. BS4 3NZ to the fitting location. For these doors BCC will be responsible for all on site measurements prior to the ordering/ manufacture of the door set.

BCC will provide for all communal doors only, identification discs to be fitted at high level to one side of the door. Where required for flat doors and communal doors BCC will provide Assa Euro profile lock cylinders.

Glazed fire screens

Where the request is for a timber framed glazed fire screen, the contractor is to supply a softwood or hardwood frame to the design supplied or agreed by BCC. To meet the 30minute or 60 requirement. Glazing to be fire rated glass suitable for the location bedded in intumescent strips held in place with suitable glazing beads. The contractor will provide suitable fixings, fire retardant packing & intumescent sealants to seal between the frame and the structural openings, architraves and cover beads/ mouldings as required. The Contractor will be responsible for all on site measurements prior to the ordering/ manufacture of the screen.

Installation

Install shall include the careful removal of architraves and cover beads/mouldings from both sides of the door frame. Cutting through all sealing mastic and paint work. Removal of door and frame complete including thresholds. Making good and preparing the structural openings. Fitting of the door, frame and ironmongery shall be in accordance with Fire Door Installation Best Practice Guides and as recommended by the manufacturers. Gaps between the back of the door frame and the structural opening are to be filled with intumescent mastic, intumescent foam, Rockwall batt or other approved systems. All to be tested and certified for the situation they are being used in. The contractor will be required to provide the technical Data sheets for the materials used to confirm their suitability. Existing or new architraves, beads/ mouldings to be fitted to the frame covering all gaps around the frame. Where any plaster or render finishes are disturbed to either side of the door during the course of the work the contractor is to make good in materials to match the existing.

Decorations

Where BCC is supplying the door and frame they will be delivered with base coat stain or undercoat as a minimum. Where the contractor is supplying the door and frame they will be expected to provide them with a similar base coat or undercoat. Further decorations to finish coat will be specified on a job by job basis.

Maintenance

Through the course of this DPS framework BCC may require the contractor to carry out remedial works to existing fire doors and frames fitted over the last 6 years, as identified following condition inspections. Work could include renewing items of ironmongery, intumescent pads, closers, carrying out adjustments, frame repairs and door face repairs to ensure the door is left in good working order and maintains its fire safety rating. Contractors will need to prove they are BM TRADA Q-Mark Fire Door maintenance scheme certified or other similar scheme.

Meter Cupboard doors

Where the request is for the supply and fit of fire resistant meter cupboard doors, the contractor is to fit minimum 60 minute fire resistand metal meter cover doors over the existing box doors. Covers to comply with the EN1363-1 & EN1366-3 60 minute fire test. The covers to be fitted directly onto the surrounding structure as per the manufacturers instructions.

### SPECIFICATION FOR NEW FIRE DOORS IN BLOCKS

## 1.1

British Standard requirements

Where possible, fire doors should meet the requirements of the necessary British Standards which include BS476 part 22: 1987 – British Standards covering fire safety and BS5588: Fire precautions in design and construction of buildings.  This guidance has taken these requirements into consideration.

Building regulations

Approved Document B - Fire and smoke containment with respect to means of escape and Approved Document M – Access to and use of buildings, set out requirements for the provision of fire doors / doors and must be complied with where appropriate.

# 2. General Fire Door & Frame Requirements

Fire doors are required to reduce the spread of fire and smoke between various parts of the building. This will ensure that occupiers and/or visitors will be able to escape from fire, via a route protected by fire resisting materials and doors.

## 2.2	Fire doors

Replace the existing door(s) to the room(s) which are indicated '30s' with 30 minute fire resisting door assemblies.  Otherwise, doors which are indicated '60s' on any attached plan or specification with 60 minute fire resisting door assemblies. All doors to be certified to comply with the relevant parts of BS 476: Part 22: 1987.

The doors & frames must meet the following requirements: -

- Hung on three hinges

- Self-closing

- Self-latching (where latch is fitted)

- Intumescent fire seals for doors indicated ‘30’ or ‘60’or combined Intumescent fire and smoke seals for doors marked ‘30s’ or ‘60s’

- Fitted door stops or rebated frame

- A security lock or latch (if required)

g)  Fire door signs on both sides.

Flat door ironmongery specification.

| Flat Door - Ironmongery specification SPEC 1 |
| --- |
| Fittings | Specification | Intumescent required |
| Door Numerals | 75mm brass. Supplied by contractor |  |
| Flat Door Deadlock | Euro profile mortice deadlock Ref.233-31 supplied with cylinders 60 or 70mm euro profile cylinder with internal turn or key both sides | Lock Gasket – preformed wrap 2mm Gasket supplied by Lorient |
| Flat Door Lock (sash) | Euro profile mortice sash lock Ref: 334-31 with cylinders 60 or 70mm euro profile cylinder with internal turn or key both sides | Lock Gasket – preformed wrap 2mm Gasket supplied by Lorient |
| Flat Door Lever Handles ( | Hoppe Arrone Aluminium lever on concealed rectangular plate door handles. Ref: AR200S/13-SP-SAA |  |
| Flat doors Hinge | 3no. 102 X 76 x 3mm thick ball bearing stainless steel hinges (with dog tag) 1hr fire rated BSEN 1935 grade13 Ref: AR7076PVD Pk854 | Hinge PADS Gasket – Preformed Hinge Pads supplied by Lorient |
| Door viewer | 35-55mm 30 minute fire rated P B door viewer | Ref: 200DEG |
| Flat Door Closer | Rutland UK single action door closer (with three adjustment settings) Ref: TS9205 (secure with security bolts and tubular bolt provided by B.C.C) | 1mm A4 size sheet provided to be cut to form Intumescent gasket for closer |
| Letter plate | 30min Firemaster fire, smoke and security letter plate REF: RJ8042F 29063 |  |
| Letter plate cowl | Security letter plate cowl REF: LP10 29063 |  |
| Threshold bush Strip | SS Threshold seal (Door bottom ) Combined Acoustic & smoke seal 27MM Ref:IS8010SDI |  |
| 30min Door or frame rebated 5mm deep | Intumescent strip 30 Min 15 x 4 Intumescent strip Ref:LP1504D |  |
| Door stop smoke | Smoke seal Perimeter seal Ref: IS7025SI |  |
| Fire door F.D 30 | Where fit only door supplied by Bristol city council | Collect from Joiner shop or other location advised |
| Ironmongery | Where fit only Ironmongery supplied by Bristol city council | Collect from joiner shop or other location advised |
| Fire doors | To include the removal of old doors and frames from site | Contractor |

Communal door ironmongery specification

| Communal Door - Ironmongery specification SPEC 2 |
| --- |
| Fitting | Specification | Intumescent required |
| Communal doors Hinge | 3no. 100 X 75 x 3-5mm thick ball bearing stainless steel hinges 1hr fire rated BSEN 1935 grade13 Ref: AR810SSS | Hinge Pads Gaskets- preformed Hinge pads supplied by Lorient. |
| Communal Door Closer | Rutland UK single action door closer (with three adjustment settings) Ref: TS9205 (secure with security bolts and tubular bolt provided by B.C.C) | 1mm A4 size sheet provided to be cut to form Intumescent gasket for closer |
| Communal Door roller catch | Hoppe Arrone 75mm square case HD adjustable Roller bolt latch Ref: AR750-SC | Roller gasket Intumescent pre formed wrap gasket. Supplied by Lorient |
| Communal Fire door keep shut / plus location signs | Hoppe Arrone plastic 80mm square sign “Fire door keep shut ” colour -white on blue Ref: AR916A RP |  |
| Communal pull handle | Hoppe Arrone Nylon (Golden yellow) straight door pull handles with steel core Ref : AR602:425BF Sizes 425mm x 34mm diameter with concealed Fixing bolts | 2no preformed intumescent sleeves |
| Communal kick plate | Hoppe Arrone plastic square end self-adhesive Supplied. Cut to size on site Ref: AR624A |  |
| Communal push plate | Hoppe Arrone plastic square end self-adhesive Ref: AR624A |  |
| Smoke seal door | Threshold seal Ref: IS8010DI |  |
| 30min Door or frame rebated 5mm deep |  | Intumescent strip 30 Min 30MIN 15 x 4 Intumescent strip Ref:LP1504D |
| Door stop smoke / frame | Smoke Seal Perimeter seal Ref IS7025SI |  |
| Fire door F.D 30 | Where fit only Door supplied by Bristol city council | Collect from joiner shop or other advised location |  |
| Ironmongery | Ironmongery supplied by Bristol city council | Collect from joiner shop or other advised location |  |
| Fire doors | To include the removal of old doors & frames from site | Contractor |  |
| Communal Store Door - Ironmongery specification SPEC 3 |
| Fitting | Specification | Intumescent required |
| Communal doors Hinge | 3no. 100 X 75 x 3-5mm thick ball bearing stainless steel hinges 1hr fire rated BSEN 1935 grade13 Ref: AR810SSS | Hinge PADS Gasket - preformed Pads supplied by Lorient. |
| Communal Door Closer | Rutland UK single action door closer (with three adjustment settings) Ref: TS9205 (secure with security bolts and tubular bolt provided by B.C.C) | 1mm A4 size sheet provided to be cut to form Intumescent gasket for closer |
| Communal Pull Handles | Hoppe Arrone Nylon (Golden Yellow) straight door pull handles with steel core. Ref: AR602:425BF Sizes 425mm x34mm diameter with concealed fixing bolts. | 2no. preformed Intumescent gasket sleeve |
| Communal Lever Handles | Hoppe Arrone Nylon lever door handles with steel core. Ref: 8A600/20DDA |  |
| Communal Suited Deadlock or Sash lock | Suited Assa 8762 or 4A existing or provided by our in house M&E Team | 1mm A4 size sheet provided to be cut to form Intumescent gasket for lock case. (M&E ASSA) sash or Dead lock |
| Communal Push plate | Hoppe Arrone 500 x 90 Plastic square end self-adhesive push plate Ref: AR624A |  |
| Communal Kick plate | Hoppe Arrone - Plastic, square end, self-adhesive kick plate, supplied cut to size and fitted one side. Recommended size 950 x 400mm (size to suit door) Ref: AR624A |  |
| Communal Fire door keep locked / plus location signs | Hoppe Arrone plastic 80mm square sign “Fire door keep locked” colour -white on blue Ref: AR916B RP Store doors only |  |
| 30min Door or frame rebated 5mm deep |  | Intumescent strip 30 Min 30MIN 15 x 4 Intumescent strip Ref:LP1504D |
| 60min Door or frame rebated 5mm deep |  | Intumescent strip 60MIN 2x 15 x 4 Intumescent strip Ref: LP1504 60MIN or 25 x 4 Intumescent strip ref: LP2504 |
| Door stop smoke | Smoke Seal Perimeter Seal Ref IS7025SI |  |
| Smoke seal door | Threshold seal Ref:IS8010DI |  |
| Fire door F.D 30 / F.D 60 | Where fit only Door supplied by Bristol city council | Collect from joiner shop or other advised location |
| Ironmongery | Ironmongery supplied by Bristol city council | Collect from joiner shop or other advised location |
| Fire doors | To include the removal of old doors & frames from site | Contractor |
|  | Frames |  |
| Frames | Frames supplied by BCC. These may need to be dismantled and reassembled on site. Cover moulds supplied by BCC if required. All works To include the removal of any old frames from site | Collect from joiner Shop or other advised location |  |
| Screens | Screens supplied by BCC These may need to be dismantled and reassembled on site. Cover moulds supplied by BCC if required. All works To include the removal of any old frames from site | Collect from joiner Shop or other advised location |  |
| Intumescent sealant Expanding foam and Fixings | To be supplied by contractor | Sealant Ref RM310 | ????? |
| SUPPLIED ITEMS BY CONTRACTOR |
| Fire rated glass | To be supplied by contractor | Pilkington Pyroshield 2 Safety clear | Lorient Intumescent u shape gasket System 36 |
| SUPALUX PANELS Fire rated panel | To be supplied by contractor | 12.5mm Panel |  |